## Sheet1
Design of a gas network system | [25 empty] | mol % | cricital T | mixture T | critical P | mixture P
[25 empty] | metano | 68.7% | 190.6 | 171.0185 | 4.6 | 6.3915
The goal of this work is to design and simulate a municipal gsa network 4th species | [24 empty] | etano | 7.585% | 305.3 |  | 4.87
[25 empty] | propano | 1.074% | 369.9 |  | 4.25
Requirement | [24 empty] | azoto | 0.9728% | 126.2 |  | 3.39
1. Design of a natural gas network | [24 empty] | anidride carbonia | 1.673% | 304.2 |  | 7.38
2. Fluid dynamic analysis of the network | [24 empty] | Hydrogen | 20% | 33.2 |  | 13.3
Part 1
At least 15 buildings, each wuth a different volume, between 100,000 cubic meter to 500,000 cubic meter | [15 empty] | Choose a typical gas in italia: |  |  | Gas Algerino
Node | Building Num | Building Volume (m3) | Buildings type | volumetric heat transfer coefficient | T in,D(℃) | T out,act(℃) | Phi heat demand (Kw) | boiler eficiency | kWh-ch | Qd Sm3/h | Sm3/s | Md Kg/h | Kg/s |  |  | Considering the war of Russia resulting in unreliable and unsustained of Gas Russo, we chosse the Gas Algerino as the supply gas in our project, which the second largest supply source.
N8 | 1 | 260000 | old | 0.9 | 20 | -8 | 6552 | 0.88 | 7445.4545 | 863.6016 | 0.23989 | 559.4411 | 0.1554
N6 | 2 | 200000 | old | 0.9 | 20 | -8 | 5040 | 0.9 | 5600 | 649.5465 | 0.18043 | 420.7762 | 0.11688
N7 | 3 | 320000 | old | 0.9 | 20 | -8 | 8064 | 0.85 | 9487.0588 | 1100.4081 | 0.30567 | 712.8444 | 0.19801
N10 | 4 | 190000 | old | 0.9 | 20 | -8 | 4788 | 0.93 | 5148.3871 | 597.1637 | 0.16588 | 386.8426 | 0.10746 |  |  | LHV | 8.6214 | 31.037 | Density | 0.6478
N12 | 5 | 170000 | old | 0.9 | 20 | -8 | 4284 | 0.9 | 4760 | 552.1145 | 0.15337 | 357.6598 | 0.09935 |  |  |  | kwh/Sm3 | MJ/Sm3 |  | (kg/Sm3)
N14 | 6 | 180000 | new | 0.4 | 20 | -8 | 2016 | 0.94 | 2144.6809 | 248.7625 | 0.069101 | 161.1483 | 0.044763
N15 | 7 | 220000 | new | 0.4 | 20 | -8 | 2464 | 0.94 | 2621.2766 | 304.043 | 0.084456 | 196.9591 | 0.054711 |  |  | heat transfer coefficients for new and old buildings
N17 | 8 | 140000 | new | 0.4 | 20 | -8 | 1568 | 0.95 | 1650.5263 | 191.4453 | 0.053179 | 124.0183 | 0.03445 |  |  | new | 0.4 |  | W/m3K
N18 | 9 | 100000 | new | 0.4 | 20 | -8 | 1120 | 0.94 | 1191.4894 | 138.2014 | 0.038389 | 89.5269 | 0.024869 |  |  | old | 0.9
N20 | 10 | 330000 | old | 0.9 | 20 | -8 | 8316 | 0.8 | 10395 | 1205.7206 | 0.33492 | 781.0658 | 0.21696
N21 | 11 | 300000 | old | 0.9 | 20 | -8 | 7560 | 0.9 | 8400 | 974.3197 | 0.27064 | 631.1643 | 0.17532
N23 | 12 | 280000 | old | 0.9 | 20 | -8 | 7056 | 0.85 | 8301.1765 | 962.8571 | 0.26746 | 623.7388 | 0.17326
N24 | 13 | 230000 | old | 0.9 | 20 | -8 | 5796 | 0.88 | 6586.3636 | 763.9552 | 0.21221 | 494.8902 | 0.13747
N25 | 14 | 120000 | new | 0.4 | 20 | -8 | 1344 | 0.93 | 1445.1613 | 167.6249 | 0.046562 | 108.5874 | 0.030163
N27 | 15 | 360000 | new | 0.4 | 20 | -8 | 4032 | 0.88 | 4581.8182 | 531.4471 | 0.14762 | 344.2714 | 0.095631
N28 | 16 | 310000 | old | 0.9 | 20 | -8 | 7812 | 0.8 | 9765 | 1132.6467 | 0.31462 | 733.7285 | 0.20381
N30 | 17 | 340000 | new | 0.4 | 20 | -8 | 3808 | 0.94 | 4051.0638 | 469.8847 | 0.13052 | 304.3913 | 0.084553
N31 | 18 | 210000 | new | 0.4 | 20 | -8 | 2352 | 0.95 | 2475.7895 | 287.1679 | 0.079769 | 186.0274 | 0.051674
Sum | [6 empty] | 83.972 |  | 96.0502 | 11140.9106 | 3.0947 | 7217.0819 | 2.0047
[6 empty] | maybe change | MW | BOSCH
https://www.bosch-thermotechnology.com/it/it/residenziale/assistenza-e-servizi/documentazione/catalogo-prodotti/
Branchs | Connection | Length
1 | N1-N2 | 1700
2 | N2-N3 | 1650
3 | N3-N4 | 1350 | [5 empty] | the most stressed one |  |  |  |  | dPlin [bar/m] | 0.00020652
4 | N4-N8 | 1500
5 | N4-N5 | 1900 |  |  |  |  | B | Branches | Length[m] | Eq.Length[m] | Tot_Length[m] | Q[Sm3/s] | Pin(bar_g) | Pout(bar_g) | Pin(bar_a) | Pout(bar_a) | deltaP(bar) | Pin(kgf/cm2) | Pout(kgf/cm2) | R_RMP | RD | D(m) | D(mm) | A(m2) | P_m(bara) | rho_actual(kg/m3) | m_dot(kg/s) | Q_actual(m3/s) | velocity(m/s) | Max velocity check |  | Real D
6 | N5-N6 | 960 |  |  |  |  | 1 | 1-2 | 1700 | 13 | 1713 | 3.0947 | 5 | 4.6462 | 6.0133 | 5.6595 | 0.35378 | 6.1318 | 5.7711 | 0.00032076 |  | 0.23106 | 231.0573 | 0.041909 | 5.8364 | 3.7307 | 2.0047 | 0.53736 | 12.822 | ✔ |  | 300
7 | N5-N7 | 1200 |  |  |  |  | 2 | 2-3 | 1650 | 4.5 | 1654.5 | 1.2904 | 4.6462 | 4.3045 | 5.6595 | 5.3178 | 0.34169 | 5.7711 | 5.4226 | 0.0014823 |  | 0.16819 | 168.1914 | 0.022206 | 5.4886 | 3.5084 | 0.83589 | 0.23825 | 10.729 | ✔ |  | 200
8 | N4-N9 | 2300 |  |  |  |  | 3 | 3-4 | 1350 | 13 | 1363 | 1.2904 | 4.3045 | 4.023 | 5.3178 | 5.0363 | 0.28149 | 5.4226 | 5.1356 | 0.0013981 |  | 0.17024 | 170.2433 | 0.022751 | 5.177 | 3.3093 | 0.83589 | 0.25259 | 11.1022 | ✔ |  | 200
9 | N9-N10 | 1000 |  |  |  |  | 8 | 4-9 | 2300 | 6.5 | 2306.5 | 0.56437 | 4.023 | 3.5467 | 5.0363 | 4.5599 | 0.47635 | 5.1356 | 4.6499 | 0.005837 |  | 0.12656 | 126.5632 | 0.012574 | 4.7981 | 3.0671 | 0.3656 | 0.1192 | 9.4798 | ✔ |  | 150
10 | N9-N11 | 2500 |  |  |  |  | 10 | 9-11 | 2500 | 6.5 | 2506.5 | 0.39849 | 3.5467 | 3.029 | 4.5599 | 4.0423 | 0.51765 | 4.6499 | 4.122 | 0.0098578 |  | 0.11352 | 113.5242 | 0.010117 | 4.3011 | 2.7494 | 0.25814 | 0.093892 | 9.2807 | ✔ |  | 125
11 | N11-N12 | 1100 |  |  |  |  | 12 | 11-13 | 2400 | 13 | 2413 | 0.24513 | 3.029 | 2.5307 | 4.0423 | 3.5439 | 0.49834 | 4.122 | 3.6138 | 0.021051 |  | 0.096991 | 96.9906 | 0.0073846 | 3.7931 | 2.4246 | 0.15879 | 0.065491 | 8.8686 | ✔ |  | 100
12 | N11-N13 | 2400 |  |  |  |  | 15 | 13-16 | 2500 | 6.5 | 2506.5 | 0.091569 | 2.5307 | 2.013 | 3.5439 | 3.0263 | 0.51765 | 3.6138 | 3.086 | 0.10943 |  | 0.068899 | 68.8986 | 0.0037264 | 3.2851 | 2.0999 | 0.059318 | 0.028248 | 7.5804 | ✔ |  | 80
13 | N13-N14 | 1300 |  |  |  |  | 16 | 16-17 | 2000 | 0 | 2000 | 0.053179 | 2.013 | 1.6 | 3.0263 | 2.6132 | 0.41305 | 3.086 | 2.6648 | 0.25254 |  | 0.057924 | 57.9241 | 0.0026338 | 2.8198 | 1.8025 | 0.03445 | 0.019113 | 7.2565 | ✔ |  | 65
14 | N13-N15 | 1900 | [5 empty] | total | 16400 |  | 16463
15 | N13-N16 | 2500
16 | N16-N17 | 2000 | [23 empty] | Gas:
17 | N16-N18 | 1500 | [5 empty] | atmP(bar) | 1.0132 | [16 empty] | velocities within pipelines should be low enough to limit the drag of impurities and noise
18 | N2-N19 | 3300 | [5 empty] | bar | kg/cm2
19 | N19-N20 | 700 | [5 empty] | 1 | 1.0197
20 | N19-N21 | 1400 | [5 empty] | rho air | 1.225 | kg/m3
21 | N19-N22 | 2300
22 | N22-N23 | 900 | [5 empty] | t (℃) | 15
23 | N22-N24 | 1100 | [5 empty] | T (K) | 288.15
24 | N22-N25 | 1450 | [5 empty] | R(kJ/kmolK) | 8.314
25 | N2-N26 | 2200 | [5 empty] | MM (kg/kmol) | 15.28
26 | N26-N27 | 1300 | [5 empty] | Z | 0.9978
27 | N26-N28 | 800
28 | N26-N29 | 1500 | [29 empty] | Real D
29 | N29-N30 | 1800 |  |  |  |  | 17 | 16-18 | 1500 | 0 | 1500 | 0.038389 | 2.013 | 1.6 | 3.0263 | 2.6132 | 0.41305 | 3.086 | 2.6648 | 0.60933 |  | 0.04825 | 48.25 | 0.0018275 | 2.8198 | 1.8025 | 0.024869 | 0.013797 | 7.5496 | ✔ |  | 65
30 | N29-N31 | 1000 |  |  |  |  | 13 | 13-14 | 1300 | 0 | 1300 | 0.069101 | 2.5307 | 1.6 | 3.5439 | 2.6132 | 0.9307 | 3.6138 | 2.6648 | 0.59341 |  | 0.048516 | 48.5158 | 0.0018477 | 3.0786 | 1.9679 | 0.044763 | 0.022747 | 12.3107 | ✔ |  | 65
[7 empty] | 14 | 13-15 | 1900 | 0 | 1900 | 0.084456 | 2.5307 | 1.6 | 3.5439 | 2.6132 | 0.9307 | 3.6138 | 2.6648 | 0.28179 |  | 0.056622 | 56.6217 | 0.0025167 | 3.0786 | 1.9679 | 0.054711 | 0.027802 | 11.0467 | ✔ |  | 65
[7 empty] | 11 | 11-12 | 1100 | 0 | 1100 | 0.15337 | 3.029 | 1.6 | 4.0423 | 2.6132 | 1.429 | 4.122 | 2.6648 | 0.27276 |  | 0.057006 | 57.0059 | 0.002551 | 3.3278 | 2.1272 | 0.09935 | 0.046705 | 18.3085 | ✔ |  | 65
[7 empty] | 9 | 9-10 | 1000 | 0 | 1000 | 0.16588 | 3.5467 | 1.6 | 4.5599 | 2.6132 | 1.9467 | 4.6499 | 2.6648 | 0.3819 |  | 0.053161 | 53.1609 | 0.0022185 | 3.5866 | 2.2926 | 0.10746 | 0.04687 | 21.1273 | ✔ |  | 65
[7 empty] | 4 | 4-8 | 1500 | 0 | 1500 | 0.23989 | 4.023 | 1.6 | 5.0363 | 2.6132 | 2.423 | 5.1356 | 2.6648 | 0.17268 |  | 0.062677 | 62.677 | 0.0030838 | 3.8248 | 2.4449 | 0.1554 | 0.063562 | 20.6115 | ✔ |  | 80
[7 empty] | 5 | 4-5 | 1900 | 6.5 | 1906.5 | 0.4861 | 4.023 | 2.536 | 5.0363 | 3.5492 | 1.4871 | 5.1356 | 3.6192 | 0.025881 |  | 0.092922 | 92.9219 | 0.0067781 | 4.2928 | 2.744 | 0.31489 | 0.11476 | 16.9306 | ✔ |  | 125
[7 empty] | 7 | 5-7 | 1200 | 0 | 1200 | 0.30567 | 2.536 | 1.6 | 3.5492 | 2.6132 | 0.93599 | 3.6192 | 2.6648 | 0.043217 |  | 0.083545 | 83.5451 | 0.0054791 | 3.0812 | 1.9696 | 0.19801 | 0.10053 | 18.3486 | ✔ |  | 100
WITHLOOP | [6 empty] | 6 | 5-6 | 960 | 0 | 960 | 0.18043 | 2.54 | 1.6 | 3.5533 | 2.6132 | 0.94 | 3.6233 | 2.6648 | 0.1417 |  | 0.065302 | 65.3015 | 0.0033475 | 3.0833 | 1.9709 | 0.11688 | 0.059305 | 17.7163 | ✔ |  | 80
[13 empty] | plinear | 0.00077999
Real D
[7 empty] | 18 | 2-19 | 3300 | 13 | 3313 | 1.1318 | 4.6462 | 3.22 | 5.6595 | 4.2332 | 1.4262 | 5.7711 | 4.3167 | 0.003535 |  | 0.14044 | 140.4408 | 0.015483 | 4.9464 | 3.1618 | 0.73318 | 0.23189 | 14.9768 | ✔ |  | 150
[7 empty] | 21 | 19-22 | 2300 | 13 | 2313 | 0.52623 | 3.22 | 2.2242 | 4.2332 | 3.2375 | 0.99575 | 4.3167 | 3.3013 | 0.010759 |  | 0.11148 | 111.4835 | 0.0097564 | 3.7354 | 2.3877 | 0.34089 | 0.14277 | 14.6334 | ✔ |  | 125
[7 empty] | 24 | 22-25 | 1450 | 0 | 1450 | 0.046562 | 2.2242 | 1.6 | 3.2375 | 2.6132 | 0.62423 | 3.3013 | 2.6648 | 0.69554 |  | 0.046943 | 46.9434 | 0.0017299 | 2.9254 | 1.87 | 0.030163 | 0.01613 | 9.3245 | ✔ |  | 65
[7 empty] | 22 | 22-23 | 900 | 0 | 900 | 0.26746 | 2.2242 | 1.6 | 3.2375 | 2.6132 | 0.62423 | 3.3013 | 2.6648 | 0.046522 |  | 0.082277 | 82.2773 | 0.0053141 | 2.9254 | 1.87 | 0.17326 | 0.092655 | 17.4357 | ✔ |  | 100
[7 empty] | 23 | 22-24 | 1100 | 0 | 1100 | 0.21221 | 2.2242 | 1.6 | 3.2375 | 2.6132 | 0.62423 | 3.3013 | 2.6648 | 0.057997 |  | 0.078599 | 78.5986 | 0.0048495 | 2.9254 | 1.87 | 0.13747 | 0.073515 | 15.1592 | ✔ |  | 100
[7 empty] | 19 | 19-20 | 700 | 0 | 700 | 0.33492 | 3.22 | 2.5 | 4.2332 | 3.5133 | 0.71998 | 4.3167 | 3.5825 | 0.060658 |  | 0.077871 | 77.8706 | 0.0047601 | 3.8732 | 2.4759 | 0.21696 | 0.087631 | 18.4095 | × | ✔ | 100
[7 empty] | 20 | 19-21 | 1400 | 0 | 1400 | 0.27064 | 3.22 | 1.6 | 4.2332 | 2.6132 | 1.62 | 4.3167 | 2.6648 | 0.088888 |  | 0.071935 | 71.9355 | 0.0040621 | 3.4232 | 2.1882 | 0.17532 | 0.080122 | 19.724 | ✔ |  | 80
[13 empty] | plinear | 0.0004305
Real D
[7 empty] | 25 | 2-26 | 2200 | 13 | 2213 | 0.67254 | 4.6462 | 3.4249 | 5.6595 | 4.4381 | 1.2214 | 5.7711 | 4.5256 | 0.011929 |  | 0.10912 | 109.1208 | 0.0093473 | 5.0488 | 3.2273 | 0.43567 | 0.135 | 14.4423 | ✔ |  | 125
[7 empty] | 28 | 26-29 | 1500 | 6.5 | 1506.5 | 0.21029 | 3.4214 | 2.59 | 4.4347 | 3.6033 | 0.83144 | 4.5221 | 3.6743 | 0.078783 |  | 0.073759 | 73.7593 | 0.0042707 | 4.019 | 2.569 | 0.13623 | 0.053027 | 12.4164 | ✔ |  | 80
[7 empty] | 30 | 29-31 | 1000 | 0 | 1000 | 0.079769 | 2.59 | 1.6 | 3.6033 | 2.6132 | 0.99 | 3.6743 | 2.6648 | 0.63798 |  | 0.047792 | 47.7922 | 0.001793 | 3.1082 | 1.9869 | 0.051674 | 0.026008 | 14.5052 | ✔ |  | 65
[7 empty] | 29 | 29-30 | 1800 | 0 | 1800 | 0.13052 | 2.5934 | 1.6 | 3.6067 | 2.6132 | 0.99342 | 3.6778 | 2.6648 | 0.14523 |  | 0.064969 | 64.9693 | 0.0033135 | 3.11 | 1.988 | 0.084553 | 0.042533 | 12.8362 | ✔ |  | 80
[7 empty] | 27 | 26-28 | 800 | 0 | 800 | 0.31462 | 3.42 | 1.6 | 4.4333 | 2.6132 | 1.82 | 4.5207 | 2.6648 | 0.13675 |  | 0.065785 | 65.785 | 0.0033972 | 3.5232 | 2.2521 | 0.20381 | 0.090498 | 26.6388 | ✔ |  | 80
[7 empty] | 26 | 26-27 | 1300 | 0 | 1300 | 0.14762 | 3.42 | 1.6 | 4.4333 | 2.6132 | 1.82 | 4.5207 | 2.6648 | 0.33358 |  | 0.054674 | 54.6742 | 0.0023466 | 3.5232 | 2.2521 | 0.095631 | 0.042462 | 18.0954 | ✔ |  | 65
[13 empty] | plinear | 0.0005519